## Slide 1: Fundamentals of Industrial Hygiene 6th Edition
Chapter 21:
Dilution Ventilation of
Non-Industrial Workplaces
Compiled by Allen Sullivan,
Assistant Professor, Safety and Health Management Central Washington University

## Slide 2: Introduction
Industrial hygienists usually get involved with heating, ventilating, and air conditioning (HVAC) systems in response to complaints about indoor air quality (IAQ).
HVAC systems are built to provide:
  fresh air (provide sufficient oxygen)
  clean air (maintain contaminant levels at acceptable levels)
  tempered air (temperature and humidity regulation)
  maintain odors at acceptable levels

## Slide 3: Fresh Air Quantity
The recommended quantity of fresh air (cfm OA/person) has varied over the years.
In commercial buildings, heating, air conditioning, and ventilation account for about 50% of energy consumed by building.
    buildings constructed in the 1970s and 1980s
      OA supply rates as low as 5 cfm OA/person
    also:
      new building methods
      new building materials
      new furnishings
      new maintenance/cleaning products

## Slide 4: Fresh Air Quantity (cont.)
Since the 1980s, building and ventilation standards have been revised:
  IAQ considerations now a selection criterion for materials and furnishings
  building managers more aware of impacts of maintenance and landscaping activities on IAQ
  elimination of smoking in most occupancies
  more attention of role of microorganisms on IAQ
  Note: Currently, the American Society of Heating, Refrigerating, and Air-Conditioning (ASHRAE) recommends 15–20 cfm OA/person.

## Slide 5: HVAC Systems
HVAC implies mechanically ventilating, heating, cooling, humidifying, dehumidifying, and cleaning air for comfort, safety, and health.
HVAC systems also provide for odor control and maintenance of oxygen and carbon dioxide levels.
    zoned systems
    constant air-volume (CV) systems
    variable air-volume (VAV) systems
      relationship of horsepower and fan speed

## Slide 6: Zoning

## Slide 7: Terms
Heating, ventilating, and air conditioning (HVAC) system
Air-handling unit (AHU)

## Slide 8: Terms (cont.)
Occupied zone
Acceptable indoor air quality

## Slide 9: Terms (cont.)
Outdoor air (OA)
Return air (RA)
Exhaust air (EA)
Mixed air (MA)
Supply air (SA)
Bypass air (BA)

## Slide 10: Air Circulation in an HVAC System

## Slide 14: HVAC System Components
Unit ventilators
Dampers
  fire dampers
Terminal devices
  improper or malfunctioning devices
  obtaining good air mixing
  thermal comfort considerations
Return air systems
Ducts
  cleaning

## Slide 15: Indoor Air Quality Issues
The U.S. EPA attributes most IAQ problems in commercial buildings to:
  indoor air pollutants
  ventilation issues
  unintended, unplanned, or poorly planned uses of buildings

## Slide 16: HVAC Standards
  ASHRAE is the primary consensus organization that develops standards regarding HVAC systems and indoor air quality:
  ASHRAE 62.1: Ventilation for Acceptable Air Quality
  ASHRAE 55: Thermal Environmental Conditions for Human
  Occupancy
  ASHRAE 52.2: Method of Testing General Ventilation Air-
  Cleaning Devices for Removal Efficiency by
  Particle Size

## Slide 17: ASHRAE 62.1
  Standard covers design and operating guidance to achieve satisfactory IAQ:
  ventilation air shall be supplied throughout the occupied zone
  ventilation systems should be designed to prevent growth and dissemination of microorganisms
  where air-intensive activities occur (e.g., combustion sources, clothes dryers), adequate make-up air should be provided
  relative humidity should be maintained between 30% and 60%
  indoor air should not contain concentrations of contaminants known to impair health or cause discomfort

## Slide 18: ASHRAE 55
  Standard specifies conditions in which 80% or more of occupants should find the environment thermally acceptable.
  It does not address other environmental factors (e.g., air quality, contaminants).
  Attempts to predict appropriate conditions of:
    temperature
    humidity
    activity
    clothing
    air movement
    radiant heat sources

## Slide 19: ASHRAE 52.2
  Standard describes the test methods for two types of air filters used in HVAC systems:
  roughing (arrestance) filters
    remove large particles
  dust spot filters
    remove smaller particles
  performance characteristics of greatest importance in selecting an air filter:
    filter’s efficiency in removing particles from air stream
    resistance to airflow through the air filter
    time interval between filter cleaning or changing

## Slide 20: Other Regulatory Standards
  All existing buildings should have been built to comply with local building codes and fire codes in force at the time of construction or major remodeling.
  Many jurisdictions have adopted some version of ASHRAE 62.1 and 55.
  Note: The building owner or manager should have records of HVAC-related standards that applied when the building was constructed or renovated.

## Slide 21: Ensuring Proper HVAC Performance
  Most HVAC systems function properly and are never the cause of potential comfort or health problems.
  For an HVAC system to function properly over its lifetime, the following checks are required:
    commissioning (start-up)
    testing and balancing (periodic)
    maintenance (routine)

## Slide 22: Diagnosing IAQ Issues
  IAQ problems are often difficult to diagnose because of confounding factors:
  arise from general complaints by a few affected individuals
    odors, headaches, respiratory tract irritation
  indoor air contaminant levels are generally very low compared to published allowable levels
  individual health problems (e.g., flu, allergies) may be involved
  general stress from work pressures may be involved

## Slide 23: Diagnosing IAQ Issues (cont.)

## Slide 24: IAQ Issue Investigation
IAQ investigation protocols usually consist of:
  employees fill out a questionnaire or are interviewed
  initial survey is conducted (see Table 21–D in text)
  relevant records are collected and reviewed (see Table 21–C)
  walkthrough inspection is conducted (see Table 21–E in text)
  readings of temperature, relative humidity, CO2 levels, and any common contaminants are taken

## Slide 25: Measuring Building Ventilation Rates
HVAC ventilation rates are usually measured to estimate the amount of outdoor air (OA) being delivered to each area of a building.
Must first measure the total airflow to each area, and then determine the proportion of total that consists of outside air (rem. mixed air).
  two methods
    direct airflow measurements
    use of tracer technique

## Slide 26: Airflow Measurements
Very similar to measurements taken to evaluate local exhaust systems (see Chapter 19 in text).
  balometer
  velometer

## Slide 27: Determining Proportion of Outside Air
Temperature method
Carbon dioxide method

## Slide 28: Example Calculation
Given balometer readings at the terminal devices serving a work area show the total air supplied to the space is 875 ft.3/min.
  CO2 readings at the specified locations were: CO2(return) 610 ppm
  CO2(mixed) 465 ppm
  CO2(outdoor) 400 ppm
  If there are 25 people in the work area, how much outdoor air is being supplied per person?

## Slide 29: Example Calculation—Solution

## Slide 30: Tracer Techniques
Utilize stable, nontoxic, easily measured gas, ideally with a density near that of air.
  Ensure HVAC controls are set in a manner typical of the time period when workers are present.
  Set up mixing fans to circulate the air to maintain constant concentrations of tracer gas.
  Measure background levels of tracer gas (indoors and outdoors).
  Release tracer gas and allow to thoroughly mix.
  Take the initial reading and record concentration and time.
  Periodically repeat concentration measurements and record.
  Continue taking measurement until indoor and outdoor concentrations are notably different.
  Calculate the air exchange rate.
  Convert the air exchange rate into volumetric airflow by multiplying by the room volume.

## Slide 31: Typical Approach (cont.)
Air exchange rate
Volumetric air flow

## Slide 32: Example Calculation
  A tracer study using released CO2 (from a fire extinguisher) is to be performed in one large room in an office building. The test will begin after employees leave.
  Room dimensions are 50 ft. × 25 ft. × 10 ft.
  Room occupancy is usually 15, with the people performing sedentary office work.
  Outdoor CO2 level at test start was 425 ppm.
  The following CO2 levels were measured during the test:

## Slide 33: Example Calculation—Solution

## Slide 34: Example Calculation – Solution (cont.)