## Slide 1: Fundamentals of Industrial Hygiene 6th Edition
Chapter 19:
Local Exhaust Ventilation
Compiled by Allen Sullivan,
Assistant Professor, Safety and Health Management Central Washington University

## Slide 2: LEV System Components
A typical LEV system consists of:
  hoods
    point where air is drawn in to capture or control contaminants
    hood types
      capturing hoods
      enclosures
      receiving hoods
      slot hoods
      canopy hoods

## Slide 3: LEV System Components (cont.)
  ducts
    carry air between hoods, air cleaners, fan, and discharge stack
    duct considerations:
      light weight, flexible fabric ducts are not recommended
        (accumulate material and sag, collapse under suction)
      air movement is always accompanied by friction
        (contaminants tend to settle on walls of ducts)
      turbulence occurs in ducts due to changes in direction and velocity
        (may cause unnecessary pressure drops)
      fans are most efficient if incoming air is straight and uniform
        (elbows, dampers, duct junctions)

## Slide 4: LEV System Components (cont.)
  exhaust stacks
    point where air is discharged
    exhaust stack considerations:
      roof boundary wake re-entry
        (use high stack discharge velocity to address)
      crosswind-induced downdraft re-entry
        (best dispersion occurs when stack velocity is >150% wind velocity)
      wind direction re-entry
        (locate exhaust stack on downwind side of roof)

## Slide 5: LEV System Components (cont.)
  fans
    generate the suction (negative air pressure) to draw contaminated air into hoods and through ducts
    fan types
      axial flow fans
      centrifugal flow fans (quieter, cheaper, produce higher pressures)
        radial-blade fans
        forward-curved blade fans
        backward-curved blade fans

## Slide 6: LEV System Components (cont.)
  air-cleaning devices
    remove contaminants prior to discharge to the environment
    particulate air-cleaning devices
      filters
      electrostatic precipitators
      cyclones
      wet scrubbers

## Slide 7: LEV System Components (cont.)
  air-cleaning devices (cont.)
    gas and vapor air-cleaning devices
      absorption
      adsorption
      oxidation (combustion)

## Slide 8: Make-Up Air
Air that enters the workroom to replace air exhausted through the ventilation system.
  Should be supplied through a planned system rather than through random infiltration to prevent a workplace from becoming air bound.
    should exceed exhaust rate by 10%
    should flow from cleaner areas through contaminated areas
    should flow from normal temperature areas to high-heat areas
    should be introduced 8–10 feet above the floor
    should be heated in winter to about 65°F
    air inlets should be located to prevent contaminated air from entering

## Slide 9: LEV Performance Evaluation
Typical tests used to evaluate LEV performance include:
  smoke tube tests
    capture range of hoods
    identifying drafts and infiltrations into hoods
    demonstrating capture distances to workers

## Slide 10: LEV Performance Evaluation (cont.)
  velocity measures
    thermo-anemometer
    rotating vane anemometer
    swinging vane anemometer

## Slide 11: LEV Performance Evaluation (cont.)
  duct velocity traverse
    typically a velometer is used
    multiple measuring points

## Slide 12: LEV Performance Evaluation (cont.)
  static pressure measurements
    potential energy available to move air